## Slide 1
Thomas Lee1, Andy Sun2 1Institute for Data, Systems, and Society, MIT
2Sloan School of Management, Operations Research Center, MIT
t_lee@mit.edu Sep. 11, 2026 PowerUp 2026 Conference: Planning Under Uncertainty Workshop
Contingencies are the Heart of Transmission Constraints

## Slide 2
Anything missing?
Transmission & Distribution
Some types of operational uncertainty in power systems
Terminology: Variability, intermittency, uncertainty, etc. are related but distinct concepts. I will use “uncertainty” as a catch-all term here.
Supply
Demand
Wind & solar
Hydropower
Nuclear
Coal & Gas
Transmission Lines (AC & DC)
Substation transformers
Residential & commercial demands
Electric vehicles
Data centers
Examples of uncertainty:
Weather-driven availability factors
Generator outages
Fuel costs
Examples of uncertainty:
Line outages
Security constraints (n-1 transmission contingencies)
Dynamic line ratings (temperature, wind, irradiance)
Examples of uncertainty:
Weather-driven load profiles
Electric vehicle trip demands
Data center computing demands
Today’s talk
Thomas Lee
t_lee@mit.edu
Contingency-Aware Nodal Optimal Power Investments with High Temporal Resolution

## Slide 3
What are transmission contingencies (security constraints)?
NERC TPL–001
“Applicable Facility Ratings shall not be exceeded” under any “P1 Single Contingency: Loss of one... Transmission Circuit [or] Transformer”.
Normative question:
Are security constraints really necessary?
Positivist viewpoint:
Security constraints constitute the vast majority of transmission constraints. Thus, they are important to model.
Grid process | Region | % of transmission constraints caused by a contingency
Interconnection | PJM | 90%
Day-ahead market | PJM | 86%
 | ERCOT | 98%
 | CAISO | 93%
Statistics sampled from PJM System Impact Studies, and DAM congestion from July 2024.
(anti-Transource protest, Franklin County, PA, 2018)
Stricter constraints increase economic & social costs.
Security constraints are needed for reliability & resilience.
Thomas Lee
t_lee@mit.edu
Contingency-Aware Nodal Optimal Power Investments with High Temporal Resolution

## Slide 4
Base Case constraints: There are of these.
Contingency constraints: There are up to of these.
The math of transmission contingencies
1Even in a state-of-the-art ACOPF formulation (ARPA-E Grid Optimization Competition Challenge 3), transmission contingencies are expressed with a linearized DC model.
Brun, M., Lee, T., Lauinger, D., Chen, X., & Sun, X. A. (2025). Alternating methods for large-scale AC optimal power flow with unit commitment. arXiv preprint arXiv:2505.06211.
Assuming DC power flows1, branch flows can be expressed as:
Power Transfer Distribution Factors
Post-contingency flow on branch , for the loss of branch :
Line Outage Distribution Factors
( is typically 1.2)
Portion of this 1MW transfer carried by paths other than branch
Change in branch ’s flow per 1MW transfer from branch ’s (from bus)  (to bus)
Thomas Lee
t_lee@mit.edu
Contingency-Aware Nodal Optimal Power Investments with High Temporal Resolution

## Slide 5
Contingencies in generator interconnection
PJM example: Example upgrades allocated to AF1-123-5: Coastal Virginia Offshore Wind (2.6GW)
$16M upgrade project: “Wreck and rebuild 5.86 miles of 230 kV line 2028 between AF2-397 Tap to Grape Vine (Cunningham)”
Base Case
$273M upgrade project: “Wreck and rebuild existing Line 568 Ladysmith - Possum Point for single circuit”
Contingency Branch
Contingency Branches
Source: https://www.pjm.com/pjmfiles/pub/planning/project-queues/Cluster-Reports/TC1/TC1_PH1_Executive_Summary.htm
LN 581 is Chancellor-Ladysmiwth 500kV: https://www.dominionenergy.com/-/media/content/about/power-line-projects/bristers-ladysmith/pdfs/scc/applicationbristersladysmithappendix-iaiib5.pdf
Monitored Branch
Monitored Branch
Thomas Lee
t_lee@mit.edu
When you read “interconnection queue delays”
That effectively means “contingency constraints”

## Slide 6
Contingencies in the energy market
Source: https://www.ercot.com/mp/data-products/data-product-details?id=NP4-191-CD
Monitored Branch
Contingency
Branch
Thomas Lee
t_lee@mit.edu
When you read “congestion costs” or “renewables curtailment”
That effectively means “contingency constraints”

## Slide 7
How can CEMs incorporate transmission contingencies?
Zonal network with network flows.
Examples:
Benefits
In theory, n-1 transfer limits could be derived from an underlying nodal network and account (NLR ReEDS zonal and county-level transfer limits).
Drawbacks
In reality, transfer limits evolve under different loading conditions.
Contingency patterns shift based on endogenous investments.
Nodal DC power flow, derated limits.
Example:
Benefits
Nodal DC base-case power flow can be exactly represented.
Setting ratings to 70% is heuristic approximation of n-1 limits.
Drawbacks
The derating heuristic’s accuracy is not theoretically guaranteed.
Contingencies are 90% of transmission constraints.
Nodal security-constrained DC PF
Example: This work
CANOPI
(Contingency-Aware Nodal Optimal Power Investments)
Benefits
Exact representation of n-1.
Endogenously captures transfer limit changes caused by large system investments (which is the whole point of CEMs).
Research question
How could this be solved efficiently?
1,000 branches with 8,760 hours
 ~1,0002 8,760 = ~18 billion potential contingency constraints
Thomas Lee
t_lee@mit.edu
Contingency-Aware Nodal Optimal Power Investments with High Temporal Resolution

## Slide 8
CANOPI algorithm
Minimal cycle basis
Bundle method
Investment problem
Inexact oracle
Transmission correction
Evaluation
Capacities
Cuts &
Contingency violations
Full problem is (MI)NLP
Fixed- problem is large-scale LP
Line rating
Rating multiplier
LODF
Pre-outage flow on i
Implied upper bound on contingency slack:
Flow on i, for outage j
Pre-outage flow on j
Post-outage flow on i
Valid lower bound & subgradient
Solve the subproblem with a subset of contingencies
Feasible upper bound
Inexact oracle
Identifies and generates contingency constraints “on-the-fly” based on the current investment iterate.
This can be “interleaved” with the bundle method major iterations.
Avoids pre-enumerating all combinatorial contingencies.
Thomas Lee
t_lee@mit.edu
Contingency-Aware Nodal Optimal Power Investments with High Temporal Resolution

## Slide 9
191
191
154
33
27
26
Cycle basis
Thomas Lee
t_lee@mit.edu
Contingency-Aware Nodal Optimal Power Investments with High Temporal Resolution
Minimum cycle basis
Fundamental cycle basis
2,169,984 NZ
842,033 NZ
11,698 NZ
6,593 NZ (0.3% of PTDF)
Exact. No angles needed.
Minimum cycle basis
(Visualizing top 3 cycles)
PTDF (1%)
PTDF

## Slide 10
Video demo: CANOPI (Contingency-Aware Nodal Optimal Power Investments)
Co-Optimized Nodal Capacity Expansion with 8760-Hourly Resolution
Transmission & Storage
Wind & Solar
Data Center Loads
Convergence to Optimality
Thomas Lee
t_lee@mit.edu

## Slide 11
Numerical results: Heuristic methods have 130%~1,300% higher costs
Heuristic methods lead to transmission underinvestment and suboptimal siting, causing load shedding and branch violations when evaluated on “out-of-sample” SC-DCOPF.
Q: What if there’s a chance to “correct” the transmission investments (but keeping the other investments fixed)?
Q: What if we used something other than 70%?
The gap does not close.
Thomas Lee
t_lee@mit.edu
Contingency-Aware Nodal Optimal Power Investments with High Temporal Resolution

## Slide 12
Conclusion
Transmission contingencies (security constraints) are empirically important (~90% of transmission constraints) and underpin a variety of grid phenomena (interconnection delays, congestion, renewables curtailment).
  If your capacity expansion model includes nodal power flows – I encourage you to look into transmission contingencies.
  CANOPI begins to solve capacity expansion on large-scale grid networks with endogenous security-constrained DC power flow, along with high temporal resolution.
Another source of uncertainty for transmission: Dynamic line ratings
t_lee@mit.edu
sunx@mit.edu
Multi-period ACOPF + transmission contingencies
Other related works:
Contingency-Aware Nodal Optimal Power Investments with High Temporal Resolution